## Slide 1: Simatic S7-plc OPC Hardware Configuration Guide
Pre Requisites:
Simatic s7 plc.
Tia portal v15.
Simatic Net.
Note: Before proceeding with this guide, make sure that Simatic Net is installed along with tia portal

## Slide 2
Create a new project with a name of your Choice

## Slide 3
Add a new PLC/Controller

## Slide 4
From PC Systems add a new PC Station

## Slide 5
Double click on PC which should take you to Device view tab. In Device view, under user application select OPC SERVER and double click on it to add it to pc

## Slide 6
After adding OPC Server, add a communication module named ‘IE GENERAL’

## Slide 7
Click on the IE general card and specify the ip address of the PC where the OPC server would be running

## Slide 8
In network view, Double click on plc which should take you to device view section
Set a ip address to the plc.

## Slide 9
In Topology View, Establish connection between PLC and PC

## Slide 10
In Network View open CP IE properties and make sure that “Access via OPC server” is checked

## Slide 11
In Network View click on connections and right click on opc server and select add new connection

## Slide 12
Select connection type as “S7 connection”
Click on the PLC on the left and select the connection and click add

## Slide 13
After adding the connection, click on the s7_connection and under opc section, select “Maintain connection Permanently”.

## Slide 14
Click on opc Server and select OPC symbols under S7 tab and select ALL

## Slide 15
In PC properties check “Generate XDB file” and select a path to save the XDB file

## Slide 16
In PC properties check “Generate XDB file” and select a path to save the XDB file

## Slide 17
After all these configurations are done, download the program to PLC

## Slide 18
After Downloading , compile the pc which should create the XDB at the location you have set earlier in configuration

## Slide 19
Once xdb file is generated, open station configurator program, the configurator program will be available after the installation of simatic net package. This application works as opc server and should be installed on pc which is intended to be server and the ip of the pc should be same as the one configured in OPC PC configuration of plc.

## Slide 20
Use the import station option and select the xdb file

## Slide 21
After selecting the XDB file, this windows should appear. Just select OK.

## Slide 22
After configuration is done, open the OPC SCOUT application. On the left you should see the available opc servers and you can access the plc and DB and tags.
Drag and drop the tag into monitoring section
After adding tag, click monitor on, and the result should change to GOOD
Monitoring section

## Slide 23
The opc configuration has been done for anonymous access,hence for opc scout the following changes needs to be done in a xml file located at : C:\ProgramData\Siemens\SIMATIC.NET\opc2\binS7opt\SCoreS7opt.xml
In case the Programdata folder is not visible, then file change visibility options to “show hidden files”
Set Enable anonymous to TRUE and EnableUserPw to False

## Slide 24
In the same xml file change the policy setting :
Set securityPolicy to #NONE
Remove the third <SecuritySetting>